# Watertight Door with Inflatable Gasket (WK Model# WT-FD-ID) Specifications

## Part 1 – General

  - Description: Provide inflatable gasket watertight/airtight door(s) factory assembled with frame(s) and all operating components in accordance with contract specifications and approved drawings.

  - Acceptable Manufacturers: Watertight/airtight door shall be as manufactured by Walz & Krenzer, Inc

  - Acceptable Distributor: Flood gate to be distributed by Floodproofing.com (1-800-507-0865; info@floodproofing.com)

  - Standards: Comply with the provisions of the following (as applicable):

- AISC “Specifications for Design, Fabrication, and Erection of Structural Steel for Buildings”.

- The Aluminum Assoc. “Aluminum Design Manual”.

- AWS Structural Welding Code D1.1, D1.2, D1.3, D1.6.

- ASME Structural Welding Code Section IX.

- FEMA Bulletin 3-93, #102 & #114.

- ASTM A36, D2000.

- American Iron and Steel Institute (AISI) CL 304, 316, 316L.

  - Submittals:

- Manufacturers Data: Submit installation and maintenance manuals for watertight/airtight door.

- Shop Drawings: Submit shop drawings approved by licensed Professional Engineer for watertight/airtight door including dimensional plans, elevations, sections, details for all mountings/connections, and parts list.

- Calculations (optional for critical applications): Submit calculations approved by licensed Professional Engineer verifying the watertight/airtight door’s ability to withstand the design pressure loading.

- QA Submittals: Submit test reports showing compliance with specified performance characteristics.

  - Qualifications: Manufacturer shall present evidence attesting to at least ten years successful experience in the design and manufacture of similar closures.

## Part 2 – Products

- Product Description: Watertight/airtight door shall be Model WT- FD-ID as manufactured by Walz & Krenzer, Inc.

- Materials:

- Panel: A-36 steel (aluminum and stainless steel available).

- Frame: A-36 steel (aluminum and stainless steel available).

- Latches: Stainless steel sliding latch bolts

- Gasket: fabric-reinforced EPDM inflatable gasket.

- Finish: steel or aluminum panels and frames to be coated with (1) primer coat and (2) top coats of shop polyurethane system. Stainless steel to be uniform bead blast per SSPC-SP17 (other options available upon request).

- Hinges: to include bronze oil-impregnated thrust bearing and stainless steel hinge pins.

- Design:

- Design Pressure: # (in feet of water or psi). Specify seating (pushing door closed) or unseating direction (pushing door open).

- Door perimeter shall be sealed by (2) independent gaskets for redundancy in case of puncture or air leak.

- Side frames are available as angles for mounting on the exterior face of the wall surface, or as flatbars for mounting inside door jambs.

- Bottom frame is a ½” flatbar, which can be recessed ½” into floor surface to achieve a flush bottom sill.

- Corners of watertight/airtight door to have a minimum 7” radius at frame.

- Air source options (select one):

  - WK standard air manifold only. For use with manual air pump (e.g. bicycle pump) or portable compressed air tank supplied by others. Manifold includes standard automotive Schrader valve stems for inflation.

  - Rechargeable compressed air tank stored on door panel, supplied with WK standard air manifold. Does not require external air source except for re-charging tank.

  - Rechargeable compressed air tank stored on door panel, supplied with push-button manifold for easy operation.

  - All options include 0-30 psi pressure gauges.

- Installation:

  - Frame(s) shall have mounting holes for expansion or adhesive concrete anchors for installation on existing openings.

  - For new concrete pours, frame(s) shall have welded embedment anchors and/or a masonry subframe.

  - Other options included weld-on installation (field welding by installer).

- Sealing surfaces shall be uninterrupted by steps greater than 0.015”, free of cracks, and with finish lay parallel to seal.

- Options include power operation, viewing windows, locks, and remote indication/control/monitoring.

- Door size and design pressure direction shall determine the quantity and type of latches or panel stops.

- Quality Assurance:

- Perform shop dimensional & flatness tests.

- Perform shop operational test.

- Perform shop chalk test.

- Air leakage test: inflate gasket(s) and confirm no loss of pressure for 0.5 hours after settling period.

- Non-Destructive Testing (if required) options include:

  - Liquid Penetrant Test: Welds in the “potential” leak path shall be liquid penetrant inspected in accordance with Appendix VIII of Section VIII of ASME Code Div. 1.

  - Magnetic Particle Testing (MT) available for non-stainless steel.

  - Other tests are available upon request.

- Hydrostatic Test (if required): Provide hydrostatic test data certifying that the closure furnished, or a closure of similar design, has been satisfactorily tested to verify that it will withstand the designed hydrostatic pressure with no visible leakage. Available upon request.

# Part 3 – Execution

- Fabrication:

- The finished product shall be rigid, neat in appearance, and free from all defects, warps, and buckles.  All exposed joints and corners shall be well rounded.

- All welding shall be performed in accordance with the requirements of the applicable AWS or ASME standards.

- The panel gasket channel and frame sealing surface shall be flat within 1/8” with a maximum deviation of 1/16” in any 6’ length.

- All butt welds to be full penetration welds.

- Installation:

- Install watertight/airtight door in accordance with manufacturer’s instructions and approved shop drawings.

- After installation, perform field operational and chalk test per manufacturer’s instructions to verify seal.

- Finish paint (if applicable) after installation.

- Warranty: Watertight/airtight door shall operate satisfactorily and be free of defects in material and workmanship for a period of not less than one year from the date of delivery